## Official Summary
Controller | Score
DPC Transformer (Ours) | 0.02726
Bang-Bang | 0.2252
Fixed Setpoint | 0.06592
PID | 0.06736
PID With Water Reset | 0.05414
Best Baseline Per Scenario | 0.04728

## Official Per Scenario
Scenario | Building | Climate | DPC Transformer | Bang-Bang | Fixed Setpoint | PID | PID With Water Reset | Best Baseline | Best Baseline Score | Improvement Versus PID With Water Reset [%] | Improvement Versus Best Baseline [%] | DPC Comfort Term | DPC Energy Term | DPC Carbon Term
building_train_1/atlanta_2 | Building 1 | Atlanta | 0.0119 | 0.17606 | 0.02622 | 0.02565 | 0.0241 | PID With Water Reset | 0.0241 | 50.6 | 50.6 | -0.0069 | -0.0024 | -0.0026
building_train_1/denver_7 | Building 1 | Denver | 0.0074 | 0.0772 | 0.03076 | 0.03065 | 0.02992 | PID With Water Reset | 0.02992 | 75.3 | 75.3 | -0.0039 | -0.0015 | -0.002
building_train_1/fairbanks_1 | Building 1 | Fairbanks | 0.1181 | 0.28711 | 0.14749 | 0.15128 | 0.21168 | Fixed Setpoint | 0.14749 | 44.2 | 19.9 | -0.0685 | -0.0146 | -0.0351
building_train_1/phoenix_5 | Building 1 | Phoenix | 0.0633 | 0.2676 | 0.12952 | 0.15441 | 0.13354 | Fixed Setpoint | 0.12952 | 52.6 | 51.1 | -0.0476 | -0.0121 | -0.0036
building_train_1/singapore_8 | Building 1 | Singapore | 0.0239 | 0.24906 | 0.02662 | 0.03124 | 0.02815 | Fixed Setpoint | 0.02662 | 15.1 | 10.2 | -0.0163 | -0.0056 | -0.002
building_train_2/atlanta_3 | Building 2 | Atlanta | 0.016 | 0.25436 | 0.02007 | 0.02018 | 0.01998 | PID With Water Reset | 0.01998 | 19.9 | 19.9 | -0.0123 | -0.0028 | -0.001
building_train_2/denver_8 | Building 2 | Denver | 0.0231 | 0.20636 | 0.09491 | 0.06848 | 0.03978 | PID With Water Reset | 0.03978 | 41.9 | 41.9 | -0.0184 | -0.0018 | -0.0029
building_train_2/fairbanks_2 | Building 2 | Fairbanks | 0.0455 | 0.18553 | 0.09847 | 0.0933 | 0.07981 | PID With Water Reset | 0.07981 | 43 | 43 | -0.0339 | -0.0033 | -0.0082
building_train_2/phoenix_6 | Building 2 | Phoenix | 0.0305 | 0.29353 | 0.16599 | 0.10527 | 0.07083 | PID With Water Reset | 0.07083 | 56.9 | 56.9 | -0.0222 | -0.0064 | -0.0019
building_train_2/singapore_1 | Building 2 | Singapore | 0.0204 | 0.27628 | 0.02251 | 0.04401 | 0.02558 | Fixed Setpoint | 0.02251 | 20.2 | 9.4 | -0.0149 | -0.0042 | -0.0014
building_train_4/atlanta_5 | Building 4 | Atlanta | 0.0275 | 0.24998 | 0.02744 | 0.02884 | 0.02848 | Fixed Setpoint | 0.02744 | 3.5 | -0.2 | -0.02 | -0.0056 | -0.0018
building_train_4/denver_2 | Building 4 | Denver | 0.0221 | 0.15135 | 0.05981 | 0.06234 | 0.0545 | PID With Water Reset | 0.0545 | 59.5 | 59.5 | -0.016 | -0.002 | -0.0041
building_train_4/fairbanks_4 | Building 4 | Fairbanks | 0.0088 | 0.14125 | 0.0306 | 0.03194 | 0.03158 | Fixed Setpoint | 0.0306 | 72.1 | 71.2 | -0.0057 | -0.0017 | -0.0014
building_train_4/phoenix_8 | Building 4 | Phoenix | 0.0088 | 0.1521 | 0.02877 | 0.02909 | 0.02884 | Fixed Setpoint | 0.02877 | 69.5 | 69.4 | -0.0059 | -0.0018 | -0.0012
building_train_4/singapore_3 | Building 4 | Singapore | 0.0289 | 0.2476 | 0.0281 | 0.04491 | 0.03246 | Fixed Setpoint | 0.0281 | 11 | -2.8 | -0.0208 | -0.0062 | -0.0019
building_train_5/atlanta_6 | Building 5 | Atlanta | 0.0166 | 0.29449 | 0.02044 | 0.03841 | 0.0273 | Fixed Setpoint | 0.02044 | 39.2 | 18.8 | -0.0116 | -0.0037 | -0.0012
building_train_5/denver_3 | Building 5 | Denver | 0.0181 | 0.18538 | 0.11634 | 0.07263 | 0.04366 | PID With Water Reset | 0.04366 | 58.5 | 58.5 | -0.0131 | -0.0017 | -0.0033
building_train_5/fairbanks_5 | Building 5 | Fairbanks | 0.0071 | 0.20089 | 0.01702 | 0.01693 | 0.01679 | PID With Water Reset | 0.01679 | 57.7 | 57.7 | -0.0045 | -0.0017 | -0.0008
building_train_5/phoenix_1 | Building 5 | Phoenix | 0.0117 | 0.13264 | 0.03732 | 0.04474 | 0.03325 | PID With Water Reset | 0.03325 | 64.8 | 64.8 | -0.0082 | -0.0015 | -0.0021
building_train_5/singapore_4 | Building 5 | Singapore | 0.0239 | 0.30261 | 0.02384 | 0.18554 | 0.10852 | Fixed Setpoint | 0.02384 | 78 | -0.3 | -0.0176 | -0.0048 | -0.0015
building_train_7/atlanta_8 | Building 7 | Atlanta | 0.0255 | 0.20439 | 0.06356 | 0.07452 | 0.04826 | PID With Water Reset | 0.04826 | 47.2 | 47.2 | -0.0184 | -0.0023 | -0.0048
building_train_7/denver_5 | Building 7 | Denver | 0.0169 | 0.24476 | 0.13896 | 0.04304 | 0.03609 | PID With Water Reset | 0.03609 | 53.2 | 53.2 | -0.0112 | -0.004 | -0.0017
building_train_7/fairbanks_7 | Building 7 | Fairbanks | 0.0344 | 0.18642 | 0.07119 | 0.07888 | 0.05372 | PID With Water Reset | 0.05372 | 36 | 36 | -0.0253 | -0.0026 | -0.0065
building_train_7/phoenix_3 | Building 7 | Phoenix | 0.0235 | 0.27326 | 0.15992 | 0.05063 | 0.04439 | PID With Water Reset | 0.04439 | 47.1 | 47.1 | -0.0164 | -0.0051 | -0.0019
building_train_7/singapore_6 | Building 7 | Singapore | 0.0233 | 0.26816 | 0.02608 | 0.04413 | 0.03109 | Fixed Setpoint | 0.02608 | 25.1 | 10.7 | -0.0162 | -0.0052 | -0.002
building_train_8/atlanta_1 | Building 8 | Atlanta | 0.0161 | 0.21293 | 0.04061 | 0.0632 | 0.03245 | PID With Water Reset | 0.03245 | 50.4 | 50.4 | -0.0094 | -0.0023 | -0.0044
building_train_8/denver_6 | Building 8 | Denver | 0.0105 | 0.24113 | 0.02016 | 0.02024 | 0.02016 | PID With Water Reset | 0.02016 | 47.9 | 47.9 | -0.0054 | -0.0033 | -0.0018
building_train_8/fairbanks_8 | Building 8 | Fairbanks | 0.079 | 0.19806 | 0.08083 | 0.08041 | 0.07723 | PID With Water Reset | 0.07723 | -2.3 | -2.3 | -0.0486 | -0.0085 | -0.0219
building_train_8/phoenix_4 | Building 8 | Phoenix | 0.0364 | 0.30776 | 0.19971 | 0.1858 | 0.15801 | PID With Water Reset | 0.15801 | 77 | 77 | -0.0232 | -0.0097 | -0.0035
building_train_8/singapore_7 | Building 8 | Singapore | 0.0185 | 0.28781 | 0.02419 | 0.10001 | 0.05408 | Fixed Setpoint | 0.02419 | 65.8 | 23.5 | -0.0109 | -0.0053 | -0.0023

## Pre-Conditioning Check
Scenario | Building | Climate | Controller | Total Energy [kWh] | Comfort Hours Energy [kWh] | Pre-Arrival Energy, 3 H Before Comfort Start [kWh] | Other Unoccupied Hours Energy [kWh] | Non-Working Days Energy [kWh] | Pre-Arrival Share [%] | Non-Working Days Share [%] | Median Start Lead Before Comfort Hours [h] | Non-Working Days (Count) | Mean Reward Per Step [-]
building_train_1/atlanta_2 | Building 1 | Atlanta | DPC Transformer (Ours) | 1271.3 | 1234.5 | 2.5 | 25.8 | 8.5 | 0.2 | 0.7 | 0 | 3 | -0.00549
building_train_1/atlanta_2 | Building 1 | Atlanta | PID With Water Reset | 281.9 | 264 | 2.4 | 8.4 | 7.1 | 0.9 | 2.5 | 0 | 3 | -0.01952
building_train_1/denver_7 | Building 1 | Denver | DPC Transformer (Ours) | 1548 | 1517.3 | 3 | 19.6 | 8.1 | 0.2 | 0.5 | 0 | 3 | -0.00677
building_train_1/denver_7 | Building 1 | Denver | PID With Water Reset | 235.8 | 218.4 | 2.8 | 8.1 | 6.5 | 1.2 | 2.7 | 0 | 3 | -0.02722
building_train_1/fairbanks_1 | Building 1 | Fairbanks | DPC Transformer (Ours) | 32389.4 | 23727.8 | 943.2 | 253.9 | 7464.5 | 2.9 | 23 | 0 | 3 | -0.11793
building_train_1/fairbanks_1 | Building 1 | Fairbanks | PID With Water Reset | 109452.3 | 73124.3 | 4632.7 | 7208.6 | 24486.8 | 4.2 | 22.4 | 2.58 | 3 | -0.29606
building_train_1/phoenix_5 | Building 1 | Phoenix | DPC Transformer (Ours) | 4011.6 | 3928 | 10.6 | 46.3 | 26.7 | 0.3 | 0.7 | 0 | 3 | -0.05848
building_train_1/phoenix_5 | Building 1 | Phoenix | PID With Water Reset | 20273 | 18725.6 | 241.7 | 624.3 | 681.5 | 1.2 | 3.4 | 0 | 3 | -0.1357
building_train_1/singapore_8 | Building 1 | Singapore | DPC Transformer (Ours) | 2658.6 | 2610.8 | 2.6 | 37.4 | 7.9 | 0.1 | 0.3 | 0 | 3 | -0.02433
building_train_1/singapore_8 | Building 1 | Singapore | PID With Water Reset | 3547.8 | 3226.7 | 56.4 | 83 | 181.8 | 1.6 | 5.1 | 1.17 | 3 | -0.03117
building_train_2/atlanta_3 | Building 2 | Atlanta | DPC Transformer (Ours) | 2515.5 | 2475.3 | 2.3 | 30.2 | 7.7 | 0.1 | 0.3 | 0 | 3 | -0.01526
building_train_2/atlanta_3 | Building 2 | Atlanta | PID With Water Reset | 2249.6 | 2214.7 | 2.5 | 16 | 16.4 | 0.1 | 0.7 | 0 | 3 | -0.01999
building_train_2/denver_8 | Building 2 | Denver | DPC Transformer (Ours) | 7396.8 | 7327.3 | 3.5 | 45.9 | 20.1 | 0 | 0.3 | 0 | 3 | -0.02581
building_train_2/denver_8 | Building 2 | Denver | PID With Water Reset | 8765.1 | 7209.7 | 652.1 | 291.6 | 611.7 | 7.4 | 7 | 0 | 3 | -0.04612
building_train_2/fairbanks_2 | Building 2 | Fairbanks | DPC Transformer (Ours) | 19985.8 | 19522.7 | 202.2 | 205 | 55.9 | 1 | 0.3 | 0 | 3 | -0.06516
building_train_2/fairbanks_2 | Building 2 | Fairbanks | PID With Water Reset | 36188.9 | 23924.6 | 2802.9 | 3491.4 | 5970 | 7.7 | 16.5 | 0.17 | 3 | -0.11164
building_train_2/phoenix_6 | Building 2 | Phoenix | DPC Transformer (Ours) | 6183.1 | 5969.7 | 8.1 | 32.8 | 172.5 | 0.1 | 2.8 | 0 | 3 | -0.03547
building_train_2/phoenix_6 | Building 2 | Phoenix | PID With Water Reset | 31152.5 | 28662.8 | 295.8 | 944.4 | 1249.5 | 0.9 | 4 | 0 | 3 | -0.10164
building_train_2/singapore_1 | Building 2 | Singapore | DPC Transformer (Ours) | 3720.2 | 3663.1 | 2.8 | 42.1 | 12.2 | 0.1 | 0.3 | 0 | 3 | -0.01841
building_train_2/singapore_1 | Building 2 | Singapore | PID With Water Reset | 4939.8 | 4473.9 | 64.3 | 94.8 | 306.8 | 1.3 | 6.2 | 0 | 3 | -0.02342
building_train_4/atlanta_5 | Building 4 | Atlanta | DPC Transformer (Ours) | 3295.6 | 3232.4 | 4 | 46.6 | 12.7 | 0.1 | 0.4 | 0 | 3 | -0.0217
building_train_4/atlanta_5 | Building 4 | Atlanta | PID With Water Reset | 4169.5 | 3828.4 | 5.7 | 24.7 | 310.7 | 0.1 | 7.5 | 0 | 3 | -0.02798
building_train_4/denver_2 | Building 4 | Denver | DPC Transformer (Ours) | 3706.5 | 3659.7 | 3.1 | 18.3 | 25.5 | 0.1 | 0.7 | 0 | 3 | -0.01715
building_train_4/denver_2 | Building 4 | Denver | PID With Water Reset | 2769 | 2659.4 | 89.5 | 11.3 | 8.8 | 3.2 | 0.3 | 0 | 3 | -0.04948
building_train_4/fairbanks_4 | Building 4 | Fairbanks | DPC Transformer (Ours) | 2104.4 | 2071.9 | 2.7 | 20.8 | 8.8 | 0.1 | 0.4 | 0 | 3 | -0.00941
building_train_4/fairbanks_4 | Building 4 | Fairbanks | PID With Water Reset | 878.4 | 859.6 | 2.8 | 9 | 7 | 0.3 | 0.8 | 0 | 3 | -0.03161
building_train_4/phoenix_8 | Building 4 | Phoenix | DPC Transformer (Ours) | 1814.6 | 1770.6 | 2.3 | 34.1 | 7.6 | 0.1 | 0.4 | 0 | 3 | -0.00784
building_train_4/phoenix_8 | Building 4 | Phoenix | PID With Water Reset | 1041.8 | 1024.8 | 2.2 | 9.5 | 5.4 | 0.2 | 0.5 | 0 | 3 | -0.01642
building_train_4/singapore_3 | Building 4 | Singapore | DPC Transformer (Ours) | 3721.7 | 3684.4 | 2.6 | 25 | 9.7 | 0.1 | 0.3 | 0 | 3 | -0.02642
building_train_4/singapore_3 | Building 4 | Singapore | PID With Water Reset | 7300 | 6726.2 | 75.6 | 117.5 | 380.7 | 1 | 5.2 | 0 | 3 | -0.03842
building_train_5/atlanta_6 | Building 5 | Atlanta | DPC Transformer (Ours) | 3438.3 | 3363.4 | 1.2 | 67.5 | 6.2 | 0 | 0.2 | 0 | 3 | -0.01852
building_train_5/atlanta_6 | Building 5 | Atlanta | PID With Water Reset | 12985.9 | 12749.6 | 19.4 | 81 | 136 | 0.1 | 1 | 0 | 3 | -0.04949
building_train_5/denver_3 | Building 5 | Denver | DPC Transformer (Ours) | 5791.7 | 5697.9 | 2.9 | 48.2 | 42.8 | 0 | 0.7 | 0 | 3 | -0.01797
building_train_5/denver_3 | Building 5 | Denver | PID With Water Reset | 5318 | 5298.4 | 3.2 | 7.9 | 8.4 | 0.1 | 0.2 | 0 | 3 | -0.0445
building_train_5/fairbanks_5 | Building 5 | Fairbanks | DPC Transformer (Ours) | 1824.1 | 1802.1 | 1.9 | 12.7 | 7.3 | 0.1 | 0.4 | 0 | 3 | -0.00645
building_train_5/fairbanks_5 | Building 5 | Fairbanks | PID With Water Reset | 1190.1 | 1176.5 | 1.9 | 7.4 | 4.3 | 0.2 | 0.4 | 0 | 3 | -0.01382
building_train_5/phoenix_1 | Building 5 | Phoenix | DPC Transformer (Ours) | 2931.7 | 2868.6 | 2.5 | 25.1 | 35.4 | 0.1 | 1.2 | 0 | 3 | -0.0085
building_train_5/phoenix_1 | Building 5 | Phoenix | PID With Water Reset | 978.4 | 961.8 | 2.6 | 6.6 | 7.5 | 0.3 | 0.8 | 0 | 3 | -0.03182
building_train_5/singapore_4 | Building 5 | Singapore | DPC Transformer (Ours) | 3762.5 | 3685.8 | 1.2 | 69.3 | 6.3 | 0 | 0.2 | 0 | 3 | -0.02272
building_train_5/singapore_4 | Building 5 | Singapore | PID With Water Reset | 39676.7 | 38868.8 | 53.5 | 400 | 354.4 | 0.1 | 0.9 | 0 | 3 | -0.13224
building_train_7/atlanta_8 | Building 7 | Atlanta | DPC Transformer (Ours) | 3464.1 | 3423 | 2.8 | 30.3 | 7.9 | 0.1 | 0.2 | 0 | 3 | -0.0223
building_train_7/atlanta_8 | Building 7 | Atlanta | PID With Water Reset | 3859.9 | 3686.4 | 88.6 | 78.3 | 6.7 | 2.3 | 0.2 | 0 | 3 | -0.05267
building_train_7/denver_5 | Building 7 | Denver | DPC Transformer (Ours) | 1557.9 | 1532.4 | 2.2 | 17.5 | 5.8 | 0.1 | 0.4 | 0 | 3 | -0.00805
building_train_7/denver_5 | Building 7 | Denver | PID With Water Reset | 1027.1 | 1013.6 | 2 | 7.1 | 4.3 | 0.2 | 0.4 | 0 | 3 | -0.01631
building_train_7/fairbanks_7 | Building 7 | Fairbanks | DPC Transformer (Ours) | 3681.6 | 3633.3 | 2.8 | 37.1 | 8.5 | 0.1 | 0.2 | 0 | 3 | -0.02363
building_train_7/fairbanks_7 | Building 7 | Fairbanks | PID With Water Reset | 3964.6 | 3636.7 | 95.6 | 27.8 | 204.5 | 2.4 | 5.2 | 0 | 3 | -0.05917
building_train_7/phoenix_3 | Building 7 | Phoenix | DPC Transformer (Ours) | 2054.3 | 2017.2 | 1.4 | 30.6 | 5.2 | 0.1 | 0.3 | 0 | 3 | -0.01701
building_train_7/phoenix_3 | Building 7 | Phoenix | PID With Water Reset | 2698.3 | 2561.9 | 1.4 | 44.6 | 90.3 | 0.1 | 3.3 | 0 | 3 | -0.026
building_train_7/singapore_6 | Building 7 | Singapore | DPC Transformer (Ours) | 2335.6 | 2297.3 | 2.5 | 28.2 | 7.6 | 0.1 | 0.3 | 0 | 3 | -0.01863
building_train_7/singapore_6 | Building 7 | Singapore | PID With Water Reset | 2894.5 | 2528.1 | 44.2 | 83.1 | 239 | 1.5 | 8.3 | 0 | 3 | -0.02435
building_train_8/atlanta_1 | Building 8 | Atlanta | DPC Transformer (Ours) | 1806 | 1786.2 | 2.2 | 7.9 | 9.7 | 0.1 | 0.5 | 0 | 3 | -0.01
building_train_8/atlanta_1 | Building 8 | Atlanta | PID With Water Reset | 1492 | 1261.1 | 79.3 | 78.5 | 73.1 | 5.3 | 4.9 | 0 | 3 | -0.02325
building_train_8/denver_6 | Building 8 | Denver | DPC Transformer (Ours) | 1577.8 | 1557.2 | 1.9 | 13.3 | 5.4 | 0.1 | 0.3 | 0 | 3 | -0.01146
building_train_8/denver_6 | Building 8 | Denver | PID With Water Reset | 1397.3 | 1267.6 | 1.9 | 9.3 | 118.5 | 0.1 | 8.5 | 0 | 3 | -0.02242
building_train_8/fairbanks_8 | Building 8 | Fairbanks | DPC Transformer (Ours) | 10900.2 | 9091.9 | 35.8 | 73.8 | 1698.8 | 0.3 | 15.6 | 0 | 3 | -0.06497
building_train_8/fairbanks_8 | Building 8 | Fairbanks | PID With Water Reset | 15380.5 | 10199.9 | 837.8 | 595.7 | 3747.1 | 5.4 | 24.4 | 0 | 3 | -0.06551
building_train_8/phoenix_4 | Building 8 | Phoenix | DPC Transformer (Ours) | 3032.5 | 2841.4 | 27.2 | 33.1 | 130.8 | 0.9 | 4.3 | 0 | 3 | -0.0352
building_train_8/phoenix_4 | Building 8 | Phoenix | PID With Water Reset | 13979.7 | 12780.2 | 96.9 | 517.1 | 585.5 | 0.7 | 4.2 | 0 | 3 | -0.12114
building_train_8/singapore_7 | Building 8 | Singapore | DPC Transformer (Ours) | 2046.7 | 2024.5 | 2.8 | 13.4 | 6 | 0.1 | 0.3 | 0 | 3 | -0.01887
building_train_8/singapore_7 | Building 8 | Singapore | PID With Water Reset | 11901.5 | 11597.2 | 57.3 | 124 | 122.9 | 0.5 | 1 | 0 | 3 | -0.09979

## Loop Benchmark
Policy | World Model | building_train_1/fairbanks_1 | building_train_2/phoenix_6 | building_train_4/atlanta_5 | building_train_5/denver_3 | building_train_7/singapore_6 | building_train_8/phoenix_4 | Score
PID With Water Reset | - | 0.02309 | 0.06874 | 0.01648 | 0.01994 | 0.00641 | 0.11846 | 0.04219
DPC Iteration 250 | World Model v2 | 0.01667 | 0.05439 | 0.02315 | 0.01854 | 0.01162 | 0.05232 | 0.02945
DPC v1 | World Model v2 | 0.00445 | 0.03201 | 0.01281 | 0.04538 | 0.0056 | 0.03333 | 0.02226
DPC v2 | World Model v2 | 0.00677 | 0.03169 | 0.01234 | 0.03821 | 0.00523 | 0.03305 | 0.02122
DPC v3 | World Model v3 | 0.01443 | 0.02738 | 0.01257 | 0.01899 | 0.00471 | 0.02839 | 0.01774
DPC v4 | World Model v4 | 0.01466 | 0.02528 | 0.01164 | 0.01908 | 0.00631 | 0.02865 | 0.0176

## World Model Accuracy
World Model | Temperature MAE 5 Min [K] | Temperature MAE 1 H [K] | Temperature MAE 6 H [K] | Temperature MAE 12 H [K] | Persistence MAE 5 Min [K] | Persistence MAE 1 H [K] | Persistence MAE 6 H [K] | Persistence MAE 12 H [K] | Reward Correlation | Comfort Captured [%]
World Model v1 | 0.276 | 0.65 | 1.462 | 1.665 | 0.466 | 1.347 | 3.344 | 4.166 | 0.895
World Model v2 | 0.283 | 0.642 | 1.403 | 1.764 | 0.466 | 1.347 | 3.344 | 4.166 | 0.888 | 62
World Model v3 | 0.262 | 0.64 | 1.441 | 1.733 | 0.466 | 1.347 | 3.344 | 4.166 | 0.889 | 56.4
World Model v4 | 0.266 | 0.628 | 1.336 | 1.652 | 0.466 | 1.347 | 3.344 | 4.166 | 0.905 | 69